## 00_Inputs
POWERLOGIC BESS · INDIAN POWER MARKET
Industrial BESS Model — MSEDCL (Maharashtra) — all-formula workbook
Legend: blue = input you edit · yellow = key levers · black = formula · green = link to another sheet.
Mirrors github.com/jai2k701/powerlogic-bess (Modules 00 sizing · 01 dispatch · 02 revenue).
MARKET
Price day (1=Typical, 2=Summer, 3=Monsoon) | 1 | Typical day (DAM) | Representative IEX DAM shapes on the Prices sheet — assumptions, not live data
BATTERY
Power — manual (MW) | 10
Energy — manual (MWh) | 20
Use Module-00 suggested size? (1=yes, 0=manual) | 1 |  | 1 → dispatch & revenue take P/E from the 01_Sizing sheet
Round-trip efficiency | 88% |  | Losses applied on discharge
Power used by model (MW) | 7.5 |  | Feeds 02_Dispatch and 03_Revenue
Energy used by model (MWh) | 75.2394 |  | Installed (container-rounded) energy when the switch is 1
MSEDCL TARIFF — HT INDUSTRIAL (FY2026-27 ORDER)
Base energy charge (₹/kWh) | 8.44 |  | Source: MSEDCL tariff order via powerlogic DB (user)
ToD peak multiplier (17:00–24:00) | 1.2
ToD solar multiplier (09:00–17:00) | 0.85 |  | Apr–Sep −15%; set 0.75 for Oct–Mar (−25%)
Open-access adders (₹/kWh) | 3.65 |  | 33 kV: STU 0.52 + wheeling 0.81 + CSS 2.07 + green cess 0.25. 132/220 kV ≈ 2.84. 7.5% wheeling loss in kind not modelled
Peak tariff (₹/kWh) | 10.128 |  | Derived — the discharge value in the peak window
SIZING (MODULE 00)
Contract demand (MW) | 10
Night load 00–06 (MW) | 5
Day load 06–17 (MW) | 7
Evening load 17–24 (MW) | 9 |  | MSEDCL peak-window load — the replacement target
Peak coverage target | 100% |  | Share of 17–24 h consumption the BESS should serve
SoC min | 10% |  | Lower state-of-charge buffer protecting cell health
SoC max | 90% |  | Usable SoC window = SoC max − SoC min (doc: 10–90% → 80%)
SoH — design | 90% |  | Sizing holds at this State of Health (≈90% after 4,000 cycles)
Container C-rate | 0.25 |  | 0.25C = 4-h product → 1.25 MW per 5 MWh container
LOSSES — FROM THE BESS REFERENCE DOC
Transformer loss | 2%
Transmission / cable loss | 1.5%
Standby & auxiliary | 1% |  | HVAC, BMS, controls — % of throughput
External efficiency (one way) | 95.56% |  | Transformer × transmission × auxiliary ≈ 95.6%
Overall system RTE | 80.37% |  | Every 1 MWh bought returns ≈ this much at the meter (doc: ~86%)
FINANCIALS
Capex (₹ Cr per MWh) | 1.1
O&M (% of capex per year) | 1.5%
Operating days per year | 330
Battery degradation per year | 2%
Discount rate (for NPV) | 12%
OTHER VALUE STREAMS (MODULE 02)
Billing demand shaved (kVA) | 5000
Demand charge (₹/kVA/month) | 450 |  | Check your MSEDCL bill for the exact category rate
Outage cover shifted from DG (hrs/yr) | 100
DG generation cost (₹/kWh) | 28

## 01_Sizing
MODULE 00 · SIZING
BESS size to replace MSEDCL peak-window (17:00–24:00) consumption
The battery must serve the 7-hour peak AND recharge through contract-demand headroom in the other 17 hours.
RESULTS
Peak energy at 100% coverage (MWh) |  | 63 | [5 empty] | Σ min(load, contract) over 17–24 h
Recharge headroom available (MWh) |  | 63 | [5 empty] | Σ min(contract − load, BESS power at target coverage) over non-peak hours
Max feasible coverage |  | 80.37% | [5 empty] | Coverage whose grid recharge (meter ÷ ext-eff ÷ RTE ÷ ext-eff) fits the headroom
Suggested power (MW) |  | 7.5 | [5 empty] | Max BESS output in the peak window, rounded up to 0.5 MW
Energy needed — nameplate (MWh) |  | 74 | [5 empty] | Meter demand ÷ external eff ÷ (SoC window × SoH) — doc formula
Container rating (MWh) |  | 5.016 | [5 empty] | 5 MWh container from the container build-up sheet
Containers required |  | 15 | [5 empty] | Larger of energy need and C-rate power need (0.25C → 1.25 MW per container)
Installed energy (MWh) |  | 75.2394 | [5 empty] | Feeds dispatch & revenue when the Inputs switch = 1
Duration (h) |  | 10.0319 | [5 empty] | installed, vs the 7-h MSEDCL peak window
Indicative capex (₹ Cr) |  | 86.9015 | [5 empty] | on installed energy, +5% contingency
Feasibility check |  | CHECK — max feasible coverage = 80%. Raise contract demand, shed day load, or add on-site solar.
PCS CONFIGURATION — MARKET-AVAILABLE UNITS (1500 V DC CLASS)
PCS unit rating (MW) |  | 2.5 | [5 empty] | Market blocks: 0.25 (string) · 1.25 · 2.5 · 3.45 · 5.0 MW skids
Containers per PCS (block size) |  | 4 | [5 empty] | Reference doc: 1 block = 4 containers + 1 PCS
PCS sizing margin over duty |  | 20% | [5 empty] | Doc sizes the inverter at 1.20 × continuous power
Redundant units (N+1 → enter 1) |  | 0
PCS units required |  | 4 | [5 empty] | Larger of the power method and the block (containers ÷ per-PCS) method
PCS installed (MW) |  | 10
System C-rate (PCS ÷ installed energy) |  | 0.13291 | OK — within the container C-rate
CHARGING-CYCLE VALIDATION & ENERGY REALITY — INDIAN (MSEDCL) OPERATING DAY
Usable energy per cycle (MWh) |  | 54.1724 | [5 empty] | Installed × SoC window × SoH — doc: usable ≠ installed
Battery-side duty per day (MWh) |  | 52.9811 | [5 empty] | Meter demand grossed up by transformer/transmission/auxiliary
Cycles per day implied |  | 0.97801 | [5 empty] | LFP warranty ≈ 6,000–8,000 cycles: 1/day ≈ 18+ yrs, 2/day ≈ 9–10 yrs
Grid purchase per day (MWh) — energy you PAY for |  | 63 | solar window (09–17) headroom delivers 24 MWh — balance charges overnight (00–09)
Delivered at meter per day (MWh) — energy that OFFSETS tariff |  | 50.6312 | [5 empty] | Overall system RTE = delivered ÷ purchased ≈ doc's ~86% figure
Cycle verdict |  | ONE daily cycle sufficient — charge solar hours (IEX floor), discharge 17–24 peak. Standard Indian BTM pattern.
Containers if 2 cycles/day were usable |  | 8 | [5 empty] | Needs a second premium window (dual-peak states, RTM stacking) — not available under MSEDCL's single 17–24 peak
24-HOUR LOAD PROFILE | [7 empty] | Blue Override column: type a value to shape an hour individually; leave blank to use the block load.
Hour | Window | Block load (MW) | Override (MW) | Load (MW) | Servable @100% (MW) | Served by BESS (MW) | Recharge headroom (MW) | Notes
0 | Normal | 5 |  | 5 | 0 | 0 | 5
1 | Normal | 5 |  | 5 | 0 | 0 | 5
2 | Normal | 5 |  | 5 | 0 | 0 | 5
3 | Normal | 5 |  | 5 | 0 | 0 | 5
4 | Normal | 5 |  | 5 | 0 | 0 | 5
5 | Normal | 5 |  | 5 | 0 | 0 | 5
6 | Normal | 7 |  | 7 | 0 | 0 | 3
7 | Normal | 7 |  | 7 | 0 | 0 | 3
8 | Normal | 7 |  | 7 | 0 | 0 | 3
9 | Solar | 7 |  | 7 | 0 | 0 | 3
10 | Solar | 7 |  | 7 | 0 | 0 | 3
11 | Solar | 7 |  | 7 | 0 | 0 | 3
12 | Solar | 7 |  | 7 | 0 | 0 | 3
13 | Solar | 7 |  | 7 | 0 | 0 | 3
14 | Solar | 7 |  | 7 | 0 | 0 | 3
15 | Solar | 7 |  | 7 | 0 | 0 | 3
16 | Solar | 7 |  | 7 | 0 | 0 | 3
17 | Peak | 9 |  | 9 | 9 | 7.233 | 0
18 | Peak | 9 |  | 9 | 9 | 7.233 | 0
19 | Peak | 9 |  | 9 | 9 | 7.233 | 0
20 | Peak | 9 |  | 9 | 9 | 7.233 | 0
21 | Peak | 9 |  | 9 | 9 | 7.233 | 0
22 | Peak | 9 |  | 9 | 9 | 7.233 | 0
23 | Peak | 9 |  | 9 | 9 | 7.233 | 0
Headroom is evaluated at the target-coverage power (one pass); the app scans coverage levels — results match on typical profiles.

## 02_Dispatch
MODULE 01 · DISPATCH
Charge on the exchange, discharge behind the meter against MSEDCL ToD
Charges the cheapest non-peak landed hours — only while landed cost < RTE × peak tariff (marginal profitability) — then discharges through the 17–24 h peak. Single daily cycle: MSEDCL has one evening peak.
DAY RESULT
Deliverable energy target (MWh) |  | 59.6591 |  | SoC the 7-hour peak window can actually discharge
Charge hours needed |  | 8
Energy drawn from exchange (MWh) |  | 59.6591
Energy delivered in peak (MWh) |  | 52.5
Charge cost (₹/day) |  | 390698.8636 |  | landed, incl. open access
Avoided tariff value (₹/day) |  | 531720
Net saving per day (₹ lakh) |  | 1.4102
Net saving per year (₹ Cr) |  | 4.6537 |  | feeds 03_Revenue arbitrage line
Avg charge cost (₹/kWh) |  | 6.5489
Avg discharge value (₹/kWh) |  | 10.128
Effective spread after losses (₹/kWh) |  | 2.6861 |  | per kWh delivered
End-of-day state of charge |  | 0% |  | ≈0% means nothing bought that could not be sold
Hour | Window | IEX MCP (₹/kWh) | Landed (₹/kWh) | ToD tariff (₹/kWh) | Charge rank | Charge hour? | Charge (MW) | Discharge (MW) | SoC (MWh) | SoC (%) | Charge cost (₹) | Avoided (₹) | Action
0 | Normal | 4.2 | 7.85 | 8.44 | 14 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | —
1 | Normal | 3.9 | 7.55 | 8.44 | 11 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | —
2 | Normal | 3.7 | 7.35 | 8.44 | 9 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | —
3 | Normal | 3.6 | 7.25 | 8.44 | 8 | 1 | 7.5 | 0 | 7.5 | 9.968% | 54375 | 0 | CHARGE
4 | Normal | 3.5 | 7.15 | 8.44 | 7 | 1 | 7.5 | 0 | 15 | 19.94% | 53625 | 0 | CHARGE
5 | Normal | 3.8 | 7.45 | 8.44 | 10 | 0 | 0 | 0 | 15 | 19.94% | 0 | 0 | —
6 | Normal | 4.6 | 8.25 | 8.44 | 15 | 0 | 0 | 0 | 15 | 19.94% | 0 | 0 | —
7 | Normal | 5.4 | 9.05 | 8.44 | 17 | 0 | 0 | 0 | 15 | 19.94% | 0 | 0 | —
8 | Normal | 5.2 | 8.85 | 8.44 | 16 | 0 | 0 | 0 | 15 | 19.94% | 0 | 0 | —
9 | Solar | 4 | 7.65 | 7.174 | 12 | 0 | 0 | 0 | 15 | 19.94% | 0 | 0 | —
10 | Solar | 3 | 6.65 | 7.174 | 5 | 1 | 7.5 | 0 | 22.5 | 29.9% | 49875 | 0 | CHARGE
11 | Solar | 2.6 | 6.25 | 7.174 | 3 | 1 | 7.5 | 0 | 30 | 39.87% | 46875 | 0 | CHARGE
12 | Solar | 2.4 | 6.05 | 7.174 | 1 | 1 | 7.5 | 0 | 37.5 | 49.84% | 45375 | 0 | CHARGE
13 | Solar | 2.4 | 6.05 | 7.174 | 1 | 1 | 7.5 | 0 | 45 | 59.81% | 45375 | 0 | CHARGE
14 | Solar | 2.6 | 6.25 | 7.174 | 3 | 1 | 7.5 | 0 | 52.5 | 69.78% | 46875 | 0 | CHARGE
15 | Solar | 3.1 | 6.75 | 7.174 | 6 | 1 | 7.1591 | 0 | 59.6591 | 79.29% | 48323.8636 | 0 | CHARGE
16 | Solar | 4 | 7.65 | 7.174 | 12 | 0 | 0 | 0 | 59.6591 | 79.29% | 0 | 0 | —
17 | Peak | 5.6 | 9.25 | 10.128 |  | 0 | 0 | 7.5 | 51.1364 | 67.96% | 0 | 75960 | DISCHARGE
18 | Peak | 7.2 | 10.85 | 10.128 |  | 0 | 0 | 7.5 | 42.6136 | 56.64% | 0 | 75960 | DISCHARGE
19 | Peak | 8.5 | 12.15 | 10.128 |  | 0 | 0 | 7.5 | 34.0909 | 45.31% | 0 | 75960 | DISCHARGE
20 | Peak | 8.9 | 12.55 | 10.128 |  | 0 | 0 | 7.5 | 25.5682 | 33.98% | 0 | 75960 | DISCHARGE
21 | Peak | 7.8 | 11.45 | 10.128 |  | 0 | 0 | 7.5 | 17.0455 | 22.65% | 0 | 75960 | DISCHARGE
22 | Peak | 6.2 | 9.85 | 10.128 |  | 0 | 0 | 7.5 | 8.5227 | 11.33% | 0 | 75960 | DISCHARGE
23 | Peak | 5 | 8.65 | 10.128 |  | 0 | 0 | 7.5 | 0 | 0% | 0 | 75960 | DISCHARGE
Simplification vs the app: the app pairs marginal charge/discharge hours and can add a small night→morning cycle; this sheet charges the N cheapest profitable non-peak hours for the single evening peak. Difference is typically <5%.

## 03_Revenue
MODULE 02 · REVENUE MODEL
The savings case on one slide — value stack, payback, 12-year IRR
HEADLINE
Annual savings, year 1 (₹ Cr) | 7.5172
Investment (₹ Cr) | 86.9015 |  | capex incl. 5% contingency
Payback year | >12 yrs
Project IRR (12-yr) | -1.437%
NPV at discount rate (₹ Cr) | -44.5822
VALUE STACK — YEAR 1 (₹ Cr / yr)
Exchange arbitrage vs ToD tariff | 4.6537
Demand charge reduction | 2.7 |  | kVA shaved × ₹/kVA/mo × 12
Diesel backup displaced | 1.467 |  | DG hours × MW × (DG cost − grid tariff)
Gross savings | 8.8207
Less: O&M year 1 | -1.3035
Net savings year 1 | 7.5172
12-YEAR CASH FLOW (₹ Cr)
Line | Y0 | Y1 | Y2 | Y3 | Y4 | Y5 | Y6 | Y7 | Y8 | Y9 | Y10 | Y11 | Y12
Arbitrage (degrades with battery) |  | 4.6537 | 4.5606 | 4.4694 | 4.38 | 4.2924 | 4.2066 | 4.1224 | 4.04 | 3.9592 | 3.88 | 3.8024 | 3.7264
Demand charge + DG displacement |  | 4.167 | 4.167 | 4.167 | 4.167 | 4.167 | 4.167 | 4.167 | 4.167 | 4.167 | 4.167 | 4.167 | 4.167
O&M (escalates 5%/yr) |  | -1.3035 | -1.3687 | -1.4371 | -1.509 | -1.5844 | -1.6637 | -1.7468 | -1.8342 | -1.9259 | -2.0222 | -2.1233 | -2.2295
Net cash flow | -86.9015 | 7.5172 | 7.3589 | 7.1993 | 7.038 | 6.875 | 6.7099 | 6.5426 | 6.3728 | 6.2003 | 6.0248 | 5.8461 | 5.6639
Cumulative cash | -86.9015 | -79.3844 | -72.0254 | -64.8262 | -57.7881 | -50.9131 | -44.2032 | -37.6606 | -31.2878 | -25.0875 | -19.0627 | -13.2166 | -7.5527
Fixed streams held flat; arbitrage degrades with the battery; O&M escalates 5%/yr — same treatment as the app.

## 04_Container
MODULE 00A · CONTAINER BUILD-UP
5 MWh BESS container — 314 Ah LFP cell electrical build-up
Source: user's "BESS 5 MWH Container Calculation.xlsx". Edit the blue cell specs / counts and the container rating flows into 01_Sizing.
Container nameplate (MWh) |  | 5.016 |  | Cells per container |  | 4992 |  | Referenced by 01_Sizing to convert energy needed into whole containers.
DESIGN A — 52S1P (LV rack, 12 racks parallel)
Level | Series/Parallel | Nos | Of | Voltage (V) | Capacity (Ah) | Energy (Wh) | Energy (kWh) | Notes
Cell |  |  |  | 3.2 | 314 | 1004.8 | 1.0048 | 3.2 V / 314 Ah LFP — blue inputs
Module | Series | 13 | Cells | 41.6 | 314 | 13062.4 | 13.0624
Pack | Series | 4 | Modules | 166.4 | 314 | 52249.6 | 52.2496
Rack | Series | 8 | Packs | 1331.2 | 314 | 417996.8 | 417.9968 | 1,331 V DC rack, 418 kWh
Container | Parallel | 12 | Racks | 1331.2 | 3768 | 5015961.6 | 5015.9616 | 52S1P — voltage unchanged, Ah adds in parallel
DESIGN B — 104S1P (HV rack, 6 racks parallel) — alternate, same energy
Level | Series/Parallel | Nos | Of | Voltage (V) | Capacity (Ah) | Energy (Wh) | Energy (kWh) | Notes
Module | Series | 13 | Cells | 41.6 | 314 | 13062.4 | 13.0624
Pack | Series | 8 | Modules | 332.8 | 314 | 104499.2 | 104.4992
Rack | Series | 8 | Packs | 2662.4 | 314 | 835993.6 | 835.9936 | 2,662 V DC rack
Container | Parallel | 6 | Racks | 2662.4 | 1884 | 5015961.6 | 5015.9616 | 104S1P — same 5,016 kWh as Design A

## 05_Schedule96
MODULE 01A · 96-BLOCK SCHEDULE
Dispatch converted to 15-minute time blocks — RLDC / SLDC / REMC format
Block 1 = 00:00–00:15 … block 96 = 23:45–24:00. Drawal (charging) positive; behind-the-meter discharge is not an injection schedule. Copy into your REMC portal template.
Block No | Time From | Time To | IEX MCP (₹/kWh) | Charge / exchange drawal (MW) | BTM discharge (MW) | Net BESS schedule (MW) | SoC end of block (%) | Action
1 | 00:00 | 00:15 | 4.2 | 0 | 0 | 0 | 0 | —
2 | 00:15 | 00:30 | 4.2 | 0 | 0 | 0 | 0 | —
3 | 00:30 | 00:45 | 4.2 | 0 | 0 | 0 | 0 | —
4 | 00:45 | 01:00 | 4.2 | 0 | 0 | 0 | 0 | —
5 | 01:00 | 01:15 | 3.9 | 0 | 0 | 0 | 0 | —
6 | 01:15 | 01:30 | 3.9 | 0 | 0 | 0 | 0 | —
7 | 01:30 | 01:45 | 3.9 | 0 | 0 | 0 | 0 | —
8 | 01:45 | 02:00 | 3.9 | 0 | 0 | 0 | 0 | —
9 | 02:00 | 02:15 | 3.7 | 0 | 0 | 0 | 0 | —
10 | 02:15 | 02:30 | 3.7 | 0 | 0 | 0 | 0 | —
11 | 02:30 | 02:45 | 3.7 | 0 | 0 | 0 | 0 | —
12 | 02:45 | 03:00 | 3.7 | 0 | 0 | 0 | 0 | —
13 | 03:00 | 03:15 | 3.6 | 7.5 | 0 | 7.5 | 2.492 | CHARGE
14 | 03:15 | 03:30 | 3.6 | 7.5 | 0 | 7.5 | 4.9841 | CHARGE
15 | 03:30 | 03:45 | 3.6 | 7.5 | 0 | 7.5 | 7.4761 | CHARGE
16 | 03:45 | 04:00 | 3.6 | 7.5 | 0 | 7.5 | 9.9682 | CHARGE
17 | 04:00 | 04:15 | 3.5 | 7.5 | 0 | 7.5 | 12.4602 | CHARGE
18 | 04:15 | 04:30 | 3.5 | 7.5 | 0 | 7.5 | 14.9523 | CHARGE
19 | 04:30 | 04:45 | 3.5 | 7.5 | 0 | 7.5 | 17.4443 | CHARGE
20 | 04:45 | 05:00 | 3.5 | 7.5 | 0 | 7.5 | 19.9364 | CHARGE
21 | 05:00 | 05:15 | 3.8 | 0 | 0 | 0 | 19.9364 | —
22 | 05:15 | 05:30 | 3.8 | 0 | 0 | 0 | 19.9364 | —
23 | 05:30 | 05:45 | 3.8 | 0 | 0 | 0 | 19.9364 | —
24 | 05:45 | 06:00 | 3.8 | 0 | 0 | 0 | 19.9364 | —
25 | 06:00 | 06:15 | 4.6 | 0 | 0 | 0 | 19.9364 | —
26 | 06:15 | 06:30 | 4.6 | 0 | 0 | 0 | 19.9364 | —
27 | 06:30 | 06:45 | 4.6 | 0 | 0 | 0 | 19.9364 | —
28 | 06:45 | 07:00 | 4.6 | 0 | 0 | 0 | 19.9364 | —
29 | 07:00 | 07:15 | 5.4 | 0 | 0 | 0 | 19.9364 | —
30 | 07:15 | 07:30 | 5.4 | 0 | 0 | 0 | 19.9364 | —
31 | 07:30 | 07:45 | 5.4 | 0 | 0 | 0 | 19.9364 | —
32 | 07:45 | 08:00 | 5.4 | 0 | 0 | 0 | 19.9364 | —
33 | 08:00 | 08:15 | 5.2 | 0 | 0 | 0 | 19.9364 | —
34 | 08:15 | 08:30 | 5.2 | 0 | 0 | 0 | 19.9364 | —
35 | 08:30 | 08:45 | 5.2 | 0 | 0 | 0 | 19.9364 | —
36 | 08:45 | 09:00 | 5.2 | 0 | 0 | 0 | 19.9364 | —
37 | 09:00 | 09:15 | 4 | 0 | 0 | 0 | 19.9364 | —
38 | 09:15 | 09:30 | 4 | 0 | 0 | 0 | 19.9364 | —
39 | 09:30 | 09:45 | 4 | 0 | 0 | 0 | 19.9364 | —
40 | 09:45 | 10:00 | 4 | 0 | 0 | 0 | 19.9364 | —
41 | 10:00 | 10:15 | 3 | 7.5 | 0 | 7.5 | 22.4284 | CHARGE
42 | 10:15 | 10:30 | 3 | 7.5 | 0 | 7.5 | 24.9204 | CHARGE
43 | 10:30 | 10:45 | 3 | 7.5 | 0 | 7.5 | 27.4125 | CHARGE
44 | 10:45 | 11:00 | 3 | 7.5 | 0 | 7.5 | 29.9045 | CHARGE
45 | 11:00 | 11:15 | 2.6 | 7.5 | 0 | 7.5 | 32.3966 | CHARGE
46 | 11:15 | 11:30 | 2.6 | 7.5 | 0 | 7.5 | 34.8886 | CHARGE
47 | 11:30 | 11:45 | 2.6 | 7.5 | 0 | 7.5 | 37.3807 | CHARGE
48 | 11:45 | 12:00 | 2.6 | 7.5 | 0 | 7.5 | 39.8727 | CHARGE
49 | 12:00 | 12:15 | 2.4 | 7.5 | 0 | 7.5 | 42.3648 | CHARGE
50 | 12:15 | 12:30 | 2.4 | 7.5 | 0 | 7.5 | 44.8568 | CHARGE
51 | 12:30 | 12:45 | 2.4 | 7.5 | 0 | 7.5 | 47.3488 | CHARGE
52 | 12:45 | 13:00 | 2.4 | 7.5 | 0 | 7.5 | 49.8409 | CHARGE
53 | 13:00 | 13:15 | 2.4 | 7.5 | 0 | 7.5 | 52.3329 | CHARGE
54 | 13:15 | 13:30 | 2.4 | 7.5 | 0 | 7.5 | 54.825 | CHARGE
55 | 13:30 | 13:45 | 2.4 | 7.5 | 0 | 7.5 | 57.317 | CHARGE
56 | 13:45 | 14:00 | 2.4 | 7.5 | 0 | 7.5 | 59.8091 | CHARGE
57 | 14:00 | 14:15 | 2.6 | 7.5 | 0 | 7.5 | 62.3011 | CHARGE
58 | 14:15 | 14:30 | 2.6 | 7.5 | 0 | 7.5 | 64.7932 | CHARGE
59 | 14:30 | 14:45 | 2.6 | 7.5 | 0 | 7.5 | 67.2852 | CHARGE
60 | 14:45 | 15:00 | 2.6 | 7.5 | 0 | 7.5 | 69.7772 | CHARGE
61 | 15:00 | 15:15 | 3.1 | 7.1591 | 0 | 7.1591 | 72.156 | CHARGE
62 | 15:15 | 15:30 | 3.1 | 7.1591 | 0 | 7.1591 | 74.5348 | CHARGE
63 | 15:30 | 15:45 | 3.1 | 7.1591 | 0 | 7.1591 | 76.9136 | CHARGE
64 | 15:45 | 16:00 | 3.1 | 7.1591 | 0 | 7.1591 | 79.2923 | CHARGE
65 | 16:00 | 16:15 | 4 | 0 | 0 | 0 | 79.2923 | —
66 | 16:15 | 16:30 | 4 | 0 | 0 | 0 | 79.2923 | —
67 | 16:30 | 16:45 | 4 | 0 | 0 | 0 | 79.2923 | —
68 | 16:45 | 17:00 | 4 | 0 | 0 | 0 | 79.2923 | —
69 | 17:00 | 17:15 | 5.6 | 0 | 7.5 | -7.5 | 76.4605 | DISCHARGE
70 | 17:15 | 17:30 | 5.6 | 0 | 7.5 | -7.5 | 73.6286 | DISCHARGE
71 | 17:30 | 17:45 | 5.6 | 0 | 7.5 | -7.5 | 70.7967 | DISCHARGE
72 | 17:45 | 18:00 | 5.6 | 0 | 7.5 | -7.5 | 67.9649 | DISCHARGE
73 | 18:00 | 18:15 | 7.2 | 0 | 7.5 | -7.5 | 65.133 | DISCHARGE
74 | 18:15 | 18:30 | 7.2 | 0 | 7.5 | -7.5 | 62.3011 | DISCHARGE
75 | 18:30 | 18:45 | 7.2 | 0 | 7.5 | -7.5 | 59.4692 | DISCHARGE
76 | 18:45 | 19:00 | 7.2 | 0 | 7.5 | -7.5 | 56.6374 | DISCHARGE
77 | 19:00 | 19:15 | 8.5 | 0 | 7.5 | -7.5 | 53.8055 | DISCHARGE
78 | 19:15 | 19:30 | 8.5 | 0 | 7.5 | -7.5 | 50.9736 | DISCHARGE
79 | 19:30 | 19:45 | 8.5 | 0 | 7.5 | -7.5 | 48.1418 | DISCHARGE
80 | 19:45 | 20:00 | 8.5 | 0 | 7.5 | -7.5 | 45.3099 | DISCHARGE
81 | 20:00 | 20:15 | 8.9 | 0 | 7.5 | -7.5 | 42.478 | DISCHARGE
82 | 20:15 | 20:30 | 8.9 | 0 | 7.5 | -7.5 | 39.6462 | DISCHARGE
83 | 20:30 | 20:45 | 8.9 | 0 | 7.5 | -7.5 | 36.8143 | DISCHARGE
84 | 20:45 | 21:00 | 8.9 | 0 | 7.5 | -7.5 | 33.9824 | DISCHARGE
85 | 21:00 | 21:15 | 7.8 | 0 | 7.5 | -7.5 | 31.1506 | DISCHARGE
86 | 21:15 | 21:30 | 7.8 | 0 | 7.5 | -7.5 | 28.3187 | DISCHARGE
87 | 21:30 | 21:45 | 7.8 | 0 | 7.5 | -7.5 | 25.4868 | DISCHARGE
88 | 21:45 | 22:00 | 7.8 | 0 | 7.5 | -7.5 | 22.655 | DISCHARGE
89 | 22:00 | 22:15 | 6.2 | 0 | 7.5 | -7.5 | 19.8231 | DISCHARGE
90 | 22:15 | 22:30 | 6.2 | 0 | 7.5 | -7.5 | 16.9912 | DISCHARGE
91 | 22:30 | 22:45 | 6.2 | 0 | 7.5 | -7.5 | 14.1593 | DISCHARGE
92 | 22:45 | 23:00 | 6.2 | 0 | 7.5 | -7.5 | 11.3275 | DISCHARGE
93 | 23:00 | 23:15 | 5 | 0 | 7.5 | -7.5 | 8.4956 | DISCHARGE
94 | 23:15 | 23:30 | 5 | 0 | 7.5 | -7.5 | 5.6637 | DISCHARGE
95 | 23:30 | 23:45 | 5 | 0 | 7.5 | -7.5 | 2.8319 | DISCHARGE
96 | 23:45 | 24:00 | 5 | 0 | 7.5 | -7.5 | 0 | DISCHARGE
SoC is interpolated linearly inside each hour. MW values repeat across the four blocks of an hour — the dispatch plan is hourly; refine block-wise in RTM if needed.

## Prices
Hour | Typical day (DAM) | Summer high-demand day | Monsoon / flat day
0 | 4.2 | 5 | 3.8
1 | 3.9 | 4.6 | 3.6
2 | 3.7 | 4.4 | 3.5
3 | 3.6 | 4.3 | 3.4
4 | 3.5 | 4.4 | 3.4
5 | 3.8 | 4.8 | 3.6
6 | 4.6 | 5.8 | 4
7 | 5.4 | 6.8 | 4.4
8 | 5.2 | 6.2 | 4.4
9 | 4 | 4.6 | 4
10 | 3 | 3.2 | 3.7
11 | 2.6 | 2.6 | 3.5
12 | 2.4 | 2.3 | 3.4
13 | 2.4 | 2.2 | 3.4
14 | 2.6 | 2.5 | 3.5
15 | 3.1 | 3.4 | 3.7
16 | 4 | 5.2 | 4.1
17 | 5.6 | 7.4 | 4.7
18 | 7.2 | 9.6 | 5.4
19 | 8.5 | 10 | 5.8
20 | 8.9 | 10 | 5.7
21 | 7.8 | 9.2 | 5.2
22 | 6.2 | 7.4 | 4.6
23 | 5 | 6 | 4.1
Representative IEX day-ahead price shapes (₹/kWh) — hardcoded assumptions, not live market data. Source: PowerLogic BESS app (github.com/jai2k701/powerlogic-bess).